Request For Information (RFI) Flue gas purification at waste-to-energy plant (WtEP) IVBO – Bruges

1 General provisions

This market study (RFI) does not relate to a government contract under the procurement regulations, but is a request made in the context of a market study to obtain information about a specific product, service or activity.

1.1 Definitions

| Abbreviations | Description |
| --- | --- |
| AEC | Waste-to-energy plant |
| BREF | Best Available Technology for Waste Incineration Plants as included in Chapter 3.16. Waste Incineration, Part 3 of Title III of the VLAREM. |
| IVBO | Intermunicipal partnership for waste removal and processing in Bruges and the surrounding area |
| RFI | Request for Information (=market research) |
| WOO | Law of 17 June 2016 on public procurement |

1.2 Purpose of the market study

The Intermunicipal Partnership for Waste Removal and Processing in Bruges and the Surrounding Area, hereinafter referred to as IVBO, requests information via this RFI from potentially interested market parties regarding the technical possibilities and, among other things, their economic impact on Capex and Opex for replacing an existing flue gas purification system of the current Waste-to-Energy Plant (WtEP) with a more efficient flue gas purification system that must be able to be rolled out within a project scope of the next 5 years.

For more information about the project envisaged by IVBO, see chapter Part 2 and Part 3.

IVBO has insufficient insight into the solutions, innovations and possibilities available to interested candidates with regard to flue gas purification techniques.

The purpose of this information phase is to provide IVBO with insight into, among other things, the following matters:

- To gain a better picture of the market parties;

- To gain insight into the availability and development status of possible solutions of flue gas purification techniques for the AEC.

- To understand the innovations and developments in flue gas purification techniques;

- To know the pricing of related installation and products and services (without these being binding in the context of any future government contract) both in Capex and Opex;

- Gain insight into the performance and dimensioning of various techniques in terms of emissions, energy, raw material consumption, residual products, wear parts, service life, maintenance periods;

- Gain insight into the expansion possibilities for future evolutions in the field of emissions and energy;

- Gain insight into the possibilities of implementing the installation in existing buildings and the impact on Capex and Opex;

- Gain insight into the necessary and expected implementation times from order to commissioning;

Taking into account these additional insights, the information collected, the years of operating experience and the standards of IVBO, it will then be possible for IVBO to define technical provisions that meet its needs, which can then be used to issue a public contract.

1.3 Conditions of the market study

The purpose of this market study is not to select a specific contractor for the assignment. The market exploration takes place prior to the procedure aimed at selecting a contractor. It is therefore not the intention that an application, quotation or other binding request or proposal for the assignment be submitted at this stage and/or that analyses be carried out that relate to a specific proposal regarding the execution of an assignment.

By issuing this RFI, IVBO does not enter into an agreement or contract with respect to the requested products/services/activities. Information received as a result of this RFI will not be used in the evaluation of suppliers, or their tenders, in connection with any public tenders or requests for proposals that may result therefrom.

Under no circumstances will an assignment be awarded on the basis of the information obtained.

Participation in the market study is entirely voluntary and without obligation. To the extent necessary, IVBO draws attention to the fact that participation in the market study is free of charge and that IVBO makes no commitment that any assignment or agreement with regard to the purpose of this market study will follow in the future.

Participation in the market study will in no way guarantee that your proposed and developed technology will be retained by IVBO at a later stage of an effective government contract for the conversion of the installation. Taking into account the objectives of Section 2.2 and the requirements of Part 3, IVBO may decide at an early stage not to continue with the explanatory discussions for this RFI.

The information provided through this market study will be treated confidentially and will not be used for any purpose other than acquiring market knowledge in order to produce better quality tender documents. IVBO does not include commercially sensitive information in the tender documents or specific references to participants in this market exploration. On the other hand, IVBO accepts no liability with regard to the information contained therein.

The participant cannot claim copyright protection for the information, ideas, suggestions and proposals provided in his answers. IVBO is free to include these elements in the public contract that

will be launched later, without payment of any compensation.

However, the concrete elaboration of an idea by the participant can be considered confidential.

If any part of your response to the market study is confidential, please include an explicit and reasoned statement here. When answering, you should also consider the purpose of the market study. You cannot rely on any protection with regard to intellectual property rights (or copyrights) in respect of the ideas, suggestions and proposals submitted in response to the market study which are not accompanied by an explicit statement of confidentiality.

By participating in the market study, the participant agrees to the above conditions and what is further described in this document.

1.4 Identity of the applicant

IVBO

Pathoekeweg 41

8000 Brugge

Tel : 050 456 311

E-mail: geert.dooms@ivbo.be

BE 0214.015.751

1.5 Market study process

Subsequent phases are possible during this market study and may depend on the number of interested parties.

Activity

1. Publication of market study

2. Interested market parties can ask additional questions or additional information can be provided by e-mail

3. Consolidated answers can be provided by IVBO to interested market parties by e-mail

4. The deadline for submitting a file by interested market parties, from which the explanatory discussions can commence, will be included in the publication

5. Explanatory interviews, one-on-one, are conducted with the selected market parties

6. Final conversation / final file completed submitted to IVBO by November 2025

Questions about this market exploration can be submitted at any time by e-mail to geert.dooms@ivbo.be

IVBO is not obliged to formulate a reasoned answer to every question, it can answer the questions that can provide added value or clarification for all interested market parties so that they can better assess whether or not to submit a further application. All questions that require a retained answer are shared with all market parties identified at that time. It is therefore best to let us know your interest in participating immediately by e-mail to geert.dooms@ivbo.be.

Between the publication and the deadline, further explanations can be given about this RFI via a Teams meeting. Please contact IVBO in time if you want to make use of this.

Interested market parties who wish to participate in this market study are requested to submit their file in digital format and must contain the following components:

- A brief introduction to the company

- The range of products and services it provides;

- References from previous years with value and description of the part that was carried out in-house (adjusted amount of part of the project that was carried out in-house if the contract was only part of a larger project)

- Describe an initial clear proposal for a possible installation structure that could meet IVBO's expectations, including the initial technical explanation of the purification technique itself.

IVBO will use this first file to determine whether more extensive information discussions will be initiated. This exchange of information and discussions should ultimately lead to a complete file with a realistic estimate of the required CAPEX and OPEX of this project and provide an answer to point 2.2 Objective and the further technical summary in part 3.

IVBO will start explanatory talks with the market parties it has retained, depending on the candidates. The talks should be finalized by November 2025.

IVBO is not obliged to accept all invitations to participate. It can limit itself to those participants who, based on the information provided, best meet the needs of the market study. IVBO can always decide during the explanatory discussions whether or not to continue the exchange of information.

Given that IVBO has already conducted internal studies on flue gas purification techniques, has already questioned market parties for this and has already initiated contacts with interested parties in its search for market parties, these market parties can still offer to participate or discussions can be continued. The final processing will be continued together with the newly submitted files.

Part 2 Project Information

2.1 General

IVBO wishes to conduct a study into possible flue gas purification techniques to replace the current system. The plant was started up in 1982 with only one purification stage and limited water purification. The installation has been expanded over the years to the model below. This concerns a wet flue gas purification system consisting of an acidic venturi scrubber with quench, a basic scrubber, flue gas reheating, sorbalite injection, sleeve filter and catalytic deNOx installation, silencer and chimney. The wastewater from the two wet washing stages is physico-chemically purified in two separate water treatments. Replacement investments have already been made over the years.

IVBO has an environmental permit until September 27, 2032.

2.2 The purpose of the renewal of the flue gas purification is:

- Guarantee the lowest possible emissions

- Guarantee the lowest possible energy consumption

- Work without waste water and without waste water discharge resulting from flue gas purification

- Obtain as few residues as possible, which are processed using an easy technique available in Belgium or which are marketed in Belgium as raw material

- Ensure the highest availability

- Obtain the simplest possible litigation

- Ensure the safest operation

- Provide for the possibility to build in Carbon Capture.

Part 3 Description and technical information of the AEC and the expected performance and information

3.1 History AEC

- In 1981 the waste energy plant (WEP) was started, there was only an acid washing tower with venturi, the waste water was purified in one settler and discharged into the canal. All fresh water came from the canal, heating network present and from 1983 the turbine worked 4.2MW counter pressure

- In 1993, the water purification was expanded with an additional physico-chemical water purification and most of the water was recovered. From then on, it was discharged to the Aquafin water purification plant and Aquafin's grey water was used as fresh water.

- In 1998, the flue gas scrubbing was expanded, a basic scrubbing stage was added, flue gas reheating with steam and gas and a sleeve filter with sorbalite.

- In 2004, a DeNOx installation was installed to better capture NOx, additional flue gas heating with HD steam, and a flue gas-flue gas heat exchanger + natural gas burner

- In 2004 the first pull was completely renewed and adapted with refractory tiles and inconel

- In 2004 the acid washing tower column was completely renewed

- In 2005/2006 the economizers were replaced

- In 2010, water purification was expanded with a 3-stage physico-chemistry

- In 2012 a new 16 MW condensing turbine and new steam condensing circuit were installed, replacing the 4.2 MW turbine

- In 2018 the complete construction of pusher platform, air distribution and grid structure and grid were replaced

- In 2018 completely new demineralization installation

- In 2020 new buffer tank for acid washing towers

- In 2020 new start-up burners ovens

- In 2022 a completely new filter chamber press was installed

- In 2022 the NOX catalysts were regenerated

- In 2023, the wastewater from the basic washing step received its own physico-chemical purification

- In 2023 and 2024, sleeve filters were restored to extend service life by 5 years

- Completely new ash discharge conveyor belts in 2024

- In 2024 new recirculation tanks for wastewater acid washing towers

3.2 Construction of current waste incineration plant

The information below is only valid for drawing up the RFI. This information will not necessarily remain the same when drawing up a specification following this RFI. These values ​​cannot subsequently be invoked to justify any deviating results that do not meet the requirements of the specifications.

Existing Wet cleaning

- Acid scrubber (quench plus venturi scrubber) - Droplet separator - Basic gas scrubber - Reheating with steam of the flue gases from approx. 65°C (after scrubbers) to 105°C - Suction fan 1 after the gas scrubbers - Reheating with steam of the flue gases from approx. 105°C (after scrubbers) to 135°C - Natural gas burner start-up first line, heating up sleeve filter - A sleeve filter - Flue gas/flue gas heating of 135°C - Natural gas heating from 135°C to 210 to 240°C - DeNOx - Suction fan 2 after the DeNOx - Silencer - The water purification for the washer(s) discharge as a pre-treatment for the discharge of the waste water (the waste water purification is common to all lines) - Chemicals: HCl, NaOH, FeCl3, TMT-15, Poly-Electrolyte, Sorbalite, Ammonia

Number of lines: 3 pieces, completely separate from inlet to the chimney (no combined installations for multiple lines)

Type of waste:

- household waste,

- not reduced and reduced (5 to 10 cm) bulky waste,

- non-hazardous medical waste,

- commercial waste (type catering and SME)),

- residues of sorted commercial waste (piece size 2 to 4 cm)).

The composition of the waste (Cl, F, S, Hg, etc.) is not specified here due to its great heterogeneity and the difficulty of performing representative samples and analysis. The performance of the purification can be better adjusted to the data of the raw unpurified flue gases.

Calorific value of waste: lower calorific value min. 7,000 – max. 12,560 kJ/kg - design 10,470 kJ/kg (peak continuous 2023: 13,500 kJ/kg)

Waste throughput: min. 6 – max. 11 tons/h - design 9 tons/h at 10,470 kJ/kg

Combustion thermal power: min. 15.7 MW – max. 26.3 MW (peak 2023: 32 MW)

Martin’s fire  Diagram grate.

Thermal power of the boiler: 13 MW – 20 MW Denayer boiler

Boiler efficiency: 78% +/- 2% (min 66% - max 84%)

Production steam setpoint: 19 tons/h – 27 tons/h at 27 bara 336-337 °C

Stability of steam production per hour: avg. +/- 3%

O2 setpoint boiler output: 7.5 - 8.5%v/v wet

Stability O2 output boiler: setpoint +/- 9%.

Boiler outlet temperature: 210°C - 270°C with average 234°C (see histogram year 2023 in °C see also note on air leakage for Line A and B)

Histogram Line A, B and C C

Stability boiler output temperature: average. +/-5%

Under pressure boiler outlet: -3 to -5 mbar

Stability of boiler outlet pressure: average +/-10%

Combustion air: 28,000 Nm³/h – 58,000 Nm³/h

Combustion air: 3.11 Nm³ wet/kg waste – 7.33 Nm³ wet/kg waste

Expected flue gas flow rate boiler outlet: 45,000 Nm³/h wet – 80,000 Nm³/h wet (normal wet conditions not converted to 11% O2) (see also note leak air already included))

Variation at 80,000 Nm³/h +/- 8%

H2O boiler output: 11.5%v/v – 20.5%v/v wet (design 13.2%v/v wet)

Existing catalytic deNOX: built in 2004 – 1 layer of catalysts (space for 3)

In 140°C – Before burner 200°C – After burner 220°C – In chimney 164°C – After suction fan 2 172°C

Inlet temperature: 135°C to 140°C – design 165°C

Operating temperature: 205°C to 220°C – design 260°C.

Output temperature: 155 to 165°C – design 195°C

3.3 Composition of raw flue gases after boiler

Dust mg/Nm³ dry = 2000 – 10,600

HCl mg/Nm³ dry = 800 – 1,500

SO2 mg/Nm³ dry = 450 – 2,500

HF mg/Nm³ dry = 25 – 150

NOx mg/Nm³ dry = 330 – 360

Hg mg/Nm³ dry = 1 – 3

PCDD/PCDF mg/Nm³ dry = 5 – 15

Pb mg/Nm³ dry = 25

Cd mg/Nm³ dry = 0.6 – 1.5

Zn mg/Nm³ dry = 51

Cu mg/Nm³ dry = 1.6

Ni mg/Nm³ dry = 0.6

Hg mg/Nm³ dry = 0.3

As mg/Nm³ dry = 0.1

O2 real: 6 - 9 % v/v wet

O2 reference: 11% v/v dry ref.

Normal reference: 0°C, 1013 mbar

3.4 To guarantee air emissions

Our operating experience shows that for elements such as SO2 and Hg it is mainly the high peaks that are critical for achieving the standard. These peaks are shorter than half an hour or can last for several half hours, which can jeopardize continuity. We therefore ask for special attention and explanation about the technique in controlling those high peaks SO2 and Hg.

A fairly new phenomenon is the P10 or lower values ​​P2.5 or BC for fine dust and PFAS emissions. Since there are no specific standards for this, we request an explanation of the method and the removal efficiencies for these parameters..

IVBO wants to excel in achieving the lowest possible emissions in our Belgian waste incineration market. We are looking for a combination of techniques with which we can realize this. The values ​​to be guaranteed below are therefore not the known standards for the parameter in question but the limit to be the best in Belgium per parameter.

If you cannot guarantee this level, please specify the lowest possible guaranteed value of the technology.

If you need to provide additional purification stages in addition to the standard structure in order to achieve this level, please indicate the value per stage and state the additional capex and opex above your basic structure separately.

In Flanders we have the obligation to have a continuous sampling for dioxins that are analysed every 14 days. We are used to working here for 100% below the detection limit.

SO2 mg/Nm³ dry (at ref value O2): 0.20

HCl mg/Nm³ dry (at ref value O2): 0.05

Dust mg/Nm³ dry (at ref value O2): 0.14

HF mg/Nm³ dry (at ref value O2): 0.01

Cd+Tl mg/Nm³ dry (at ref value O2): <DL.

Sb+As+Pb+Cr+Co+Cu+Mn+Ni+V+Sn mg/Nm³ dry (at ref value O2): <DL

Hg mg/Nm³ dry (at ref value O2): <DL

PCDD/PCDF mg/Nm³ dry (at ref value O2): <DL

Note: measurement error already deducted

NOx mg/Nm³ dry (at ref value O2) – existing system no warranty requirements

NH3 mg/Nm³ dry (at ref value O2) – existing system no warranty requirements

PFAS ng/Nm³ dry (at ref value O2) – no known standard available – specify reference efficiency

Fine Dust P10, P2.5 and BC to be specified mg/Nm³ dry (at reference value O2) – no known standard available – specify reference efficiency

CO mg/Nm³ dry (at ref value O2) – combustion parameter

TOC mg/Nm³ dry (at ref value O2) – combustion parameter

3.5 Project period

We expect to make a final choice for this project by the end of 2025 and then be able to put a specification on the market by mid-2026.

The permit procedure and tender procedure will then run in parallel: September 2026 – June 2027

The candidates provide an initial possible indication of project planning from the moment of allocation.

Important steps can get their own timing, the detailed engineering, ordering, construction, downtime.

When planning, it should be taken into account that this is an installation in operation. We do not have the possibility to completely shut down the installation for several months. One conversion per line is indicated. There can only be 1 line in stop for conversion. Depending on the duration of the conversion of 1 line, it can be determined whether this should be converted in 1 year or in a maximum of 3 years (e.g. 1 line per year).

The necessary conversion time in consecutive calendar days is crucial to be able to make a correct estimate of the investment. Stopping time costs us money. We do not expect you to budget this cost for us. What we consider conversion time is the time from the stop of the installation to warm start-up at full capacity. In such projects in the past, a lot of attention was paid during construction to very extensive cold tests and simulation programs, which allowed for normal conditions to be worked on from the first start-up, with some adjustment of control circuits.

IVBO has a lot of space outside around the installation, certain zones can be reserved for larger construction work on site. A brief description of the construction process is useful.

3.6 Operating conditions

The design and proposed technology should take into account the operating conditions and operating experience expected by IVBO.

Each line runs: 94% of all hours in a year (0.94 x 365 x 24 h)

Unforeseen stops due to flue gas purification / flue gas transport and annexes: 4x24 hours/year/line in the first 10 years after commissioning.

Maintenance frequency: maximum 1x per year

Maximum duration of maintenance work for flue gas purification installation is 4 consecutive days of 24 hours in a total shutdown of 9 days.

There shall be no additional planned short stops between stops for this maintenance to carry out periodic replacements or cleanings.

During the period of 1 year, the electricity consumption over the flue gas purification installation may not increase due to an increase in pressure differences over the process components of the flue gas purification.

For sleeve filters, guaranteed lifespan without replacing or cleaning sleeves: 10 years. Cleaning sleeves during downtime is not considered an acceptable technique. The usual blowing off of the sleeves in normal operation to monitor a constant delta P across the sleeve filter is not considered cleaning if this is done online and without disruption to normal operation.

Use of specific sleeves for removal of dioxins and NOx is permitted. In this case, special attention is requested for the anticipated removal techniques for high peaks of mercury (Hg). Results of similar projects in waste incineration and explanations regarding operation are necessary here. It is important to know both the entry conditions and the effective emissions.

In proposals with electro filters, sleeve filters, washing towers, special attention is requested for the measures to prevent corrosion by cold bridges, corrosion by standstill, and erosion damage by abrasive in the gas flows.

Transport of loaded residues may not be via piping with bubbles or under overpressure (blower type) but must be a transport via negative pressure - suction transport, this to prevent any dust in the buildings in the event of any minimal leak.

When designing, much attention should be paid to the layout so that safe replacement of wearing parts is possible in the future. All measuring and control equipment must be easily and safely accessible and dismountable. A safety and risk analysis must be included from the design. The necessary access routes and escape routes must be included in the design.

If the proposed technique has specific known risks, these should be explained and the measures envisaged for prevention should be indicated.

IVBO now consists of 3 completely separately developed flue gas purification systems up to the 3 individual chimneys. This setup provides great flexibility and autonomy in operation. We are in favour

of maintaining this and not building installations where a certain purification stage combines different lines into one device.

New purification techniques are certainly welcome. The above operating conditions must also be guaranteed for these techniques. Reference information, research reports, technical analyses, ... all information that can give a clear picture of the status of the technique are important here. The investments are so large and the permitting process is so demanding that a high degree of demonstrability in actual business operations and on a normal scale is required.

Given the difficult labour market to find qualified personnel and the relationship with higher operating costs, the purpose is to make the process as simple as possible. Special chemical processes and the production of quality end products may require a higher level of training, require more operational staff, require own laboratory and chemist. If the proposed process requires this, this should be included in the information. IVBO's organizational structure is not yet based on this and constitutes an additional operating cost.

3.7 Consumables – replacement investments

We want to get as broad a picture as possible of the possible costs that could result from the proposed technology, so we ask for as complete a picture as possible of the possible consumables and replacement investments.

To be specified are:

Consumables – replacement investments: which machines need to be replaced and with what frequency.

Here we think of housing fans, fan impellers, motors, frequency converters. Lock chambers, electrodes, sleeves and cages, transport systems.

3.8 Chemical consumption – released residues

The proposed technology may require multiple chemical products, may release residues or may release substances that can be marketed as products. Want to obtain as broad a picture as possible of all these products, residues and products. All relevant information such as correct composition, conditions of use (e.g. max. temp. 140°C), grain size distribution, concentrations must be stated. For residues it is important that we can see where it needs to be processed. For products it is especially important to know the correct composition, whether it is sufficient to be considered a product in Flanders and the buyers on the Belgian market.

Chemical consumption: per product

Name (trade name) – chemical formula – concentration and/or composition and/or grain size distribution – required process conditions – names of 3 current suppliers – price (excl. VAT) – quantity per year.

Released residues: per residue

Name (usual) – composition – processing method available in Flanders – quantity per year – processing price €/ton

Released products: per tradable product – must meet Belgian/Flemish requirements to be considered a product.

Name (usual) – composition – applications – potential demonstrable buyers – quantity per year – market value €/ton

3.9 Energy consumption

One of the main objectives of the new installation is to have the lowest possible energy consumption, both in electricity consumption and in the use of external fuels. A detailed representation of consumption as possible is requested. If additional energy sources are necessary, we expect that these will no longer be primary non-sustainable fuels, but will be of sustainable origin.

We are only interested in the consumptions that are guaranteed with this project and not in a comparison with the current installation. We will make this evaluation ourselves.

IVBO does NOT have support burners in the first draft. We only have a starter burner at the back of the combustion chamber to light the fire. Once the firebox reaches about 200 degrees, it goes out again. Today this is possible because the flue gas purification plant is fully put into operation before the fire is lit and the flue gas emission measuring devices start measuring immediately. Emission measurements were also carried out during the entire start-up to demonstrate that the standards for dioxins and furans are also respected during start-up. With a new concept of flue gas purification it may be necessary to install support burners. The necessary investment and consumption for burners and the adjustment of the boiler walls must be included in the budget.

When selecting motors and inverters, special attention is required to provide the highest class of energy-efficient labels.

Consumption of external fuels:

If external fuels are required in the system for reheating the flue gases, for standstill heating or for support burners, the consumption for a full year with an operating time of 94% must be estimated per fuel (in MWh/year).

Since the deNOx already has natural gas burners, consumption must be calculated if the inlet temperature at the heat exchanger of the deNOX becomes lower or higher than the current level (see specs).

Consumption of electricity:

Installed capacities per machine part.

A global consumption over 1 year of operation with an operating time of 94%. At minimum nominal and maximum power. The consumption per line but also the consumption of the common components such as for the storage and discharge of residues, the storage and dosing of products.

In order to obtain a good view of the impact of the installation on the consumption of electricity by the flue gas installation itself, a calculation with the enthalpy, density, temperature profile and pressure drop profile of flue gases in duct conditions is required.

When designing the induced draft fan(s), an additional reserve for an extra flow rate of 10,000 Nm³/h of moist flue gases must be taken into account. The new flue gas purification is built on an existing

boiler from the 80s and can cause unforeseen leaking air due to circumstances (explosions on the grate). IVBO chooses to include the necessary reserve for this.

3.10 Other operating costs

If the proposed technology entails any other relevant operating costs not previously described, we expect these to be described and budgeted as well.

3.11 Supplied info

Plans: oven building – sleeve filter

Screenshots Line C dated February 2024. Flue gas line acid scrubber, basic scrubber, flue gas heating, sleeve filter, deNOx, chimney