|  |  | TOXIC GAS DETECTOR |  |  | DATASHEET NO. | 0102-IDS-6097 |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | DATE | 9-Dec-14 |
|  |  |  |  |  | REV. | 2 |
|  |  |  |  |  | PREPARED BY | WAS |
|  |  |  |  |  | CHECKED BY | NAS |
|  |  |  |  |  | APPROVED BY | AR |
| 1 | Quantity |  |  | HCL Type = 10 Nos. |  |  |
| 2 | Service |  |  | Hydrogen Chloride |  |  |
| 3 | TRANSMITTER |  |  |  |  |  |
| 4 | Sensor Type |  |  | Electrochemical Sensor |  |  |
| 5 | Sensor Mounting |  |  | Directly on Transmitter |  |  |
| 6 | Wiring |  |  | 3-Wire Transmitter |  |  |
| 7 | Supply Voltage |  |  | Loop powered 24 VDC |  |  |
| 8 | Output Type |  |  | Analog 4-20 mA |  |  |
| 9 | Display |  |  | LCD/LEDs for Status Indication (Running, Fault, Alarm etc) |  |  |
| 10 | Calibrated Range |  |  | 0-10 ppm |  |  |
| 11 | Alarm Setpoints |  |  | *VTA |  |  |
| 12 | Manufacturer / Model Number |  |  | *VTA |  |  |
| 13 | HOUSING |  |  |  |  |  |
| 14 | Body Material |  |  | Cast Aluminum |  |  |
| 15 | Cable Entry |  |  | Metric M20 x 1.5 (Note 1) |  |  |
| 16 | Hazardous Area Classification |  |  | EEx'd' IIC T4 |  |  |
| 17 | Weather Protection |  |  | IP66 |  |  |
| 18 | Mounting |  |  | Mounting Brackets (Note 2) |  |  |
| 19 | ACCESSORIES |  |  |  |  |  |
| 20 | Tag Plate |  |  | Yes - Stainless Steel (Note 3) |  |  |
| 21 | NOTES: |  |  |  |  |  |
| 1) In case of multiple entries, all spare entries shall be supplied plugged with EEx'd' certified metal plugs. |  |  |  |  |  |  |
| 2) Vendor shall provide complete installation material (nuts, bolts, etc) for mounting of detector inside cable channel in control room. |  |  |  |  |  |  |
| 3) SS tag shall be fixed to the detector using SS wire. Tag plate shall include tag number, model number and sensor data. |  |  |  |  |  |  |
| 4) Vendor shall provide complete documentation for installation and maintenance as hard copies as well as in soft form. |  |  |  |  |  |  |
| *VTA: Vendor To Advise |  |  |  |  |  |  |
| N/A: Not Applicable. |  |  |  |  |  |  |

Sheet 1 of 1