|  |  | H2S GAS DETECTOR |  |  | DATASHEET NO. | 0102-IDS-6090 |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | DATE | 9-Dec-14 |
|  |  |  |  |  | REV. | 2 |
|  |  |  |  |  | PREPARED BY | WAS |
|  |  |  |  |  | CHECKED BY | NAS |
|  |  |  |  |  | APPROVED BY | AR |
| 1 | Quantity |  |  | 04 Nos. |  |  |
| 2 | Tag Number |  |  | Refer Doc # 0102-ISL-6202 |  |  |
| 3 | Service |  |  | H2S Gas Leakage Detection |  |  |
| 4 | TRANSMITTER |  |  |  |  |  |
| 5 | Sensor Type |  |  | Metal oxide semi conductor sensor |  |  |
| 6 | Sensor Housing |  |  | Aluminum coated housing |  |  |
| 7 | Sensor Mounting |  |  | Directly on Transmitter |  |  |
| 8 | Wiring |  |  | 3-Wire Transmitter |  |  |
| 9 | Supply Voltage |  |  | 24 VDC |  |  |
| 10 | Output Type |  |  | Analog 4-20 mA |  |  |
| 11 | Display |  |  | LCD/LEDs for Status Indication (Running, Fault, Alarm etc) |  |  |
| 12 | Calibrated Range |  |  | 0 - 100 ppm |  |  |
| 13 | Alarm Setpoints |  |  | 10 ppm and 30 ppm |  |  |
| 14 | Response Time |  |  | < 30 Secs = 90% of Full Scale with 100 ppm |  |  |
| 15 | Accuracy |  |  | +/-1 ppm |  |  |
| 16 | Manufacturer / Model Number |  |  | *VTA |  |  |
| 17 | HOUSING |  |  |  |  |  |
| 18 | Body Material |  |  | Aluminum die cast with dust covers, rain / splash shields |  |  |
| 19 | Cable Entry |  |  | Metric M20 x 1.5 (Note 1) |  |  |
| 20 | Hazardous Area Classification |  |  | EEx'd' , Class I, Div2, Group C&D |  |  |
| 21 | Weather Protection |  |  | IP65 |  |  |
| 22 | Mounting |  |  | 2" Pipe Support (Note 2) |  |  |
| 23 | ACCESSORIES |  |  |  |  |  |
| 24 | Calibration Equipment / Quantity |  |  | Yes, 01 no |  |  |
| 25 | Tag Plate |  |  | Yes - Stainless Steel (Note 3) |  |  |
| 26 | NOTES: |  |  |  |  |  |
| 1) In case of multiple entries, all spare entries shall be supplied plugged with EEx'd' certified metal plugs. |  |  |  |  |  |  |
| 2) Vendor shall provide complete installation material (mounting brackets, nuts, bolts, etc) for mounting on 2" pipe support. |  |  |  |  |  |  |
| 3) SS tag shall be fixed to the detector using SS wire. Tag plate shall include tag number, model number and sensor data. |  |  |  |  |  |  |
| 4) Vendor shall provide complete documentation for installation and maintenance as hard copies as well as on CD. |  |  |  |  |  |  |
| *VTA: Vendor To Advise |  |  |  |  |  |  |
| N/A: Not Applicable. |  |  |  |  |  |  |